**Effective July 10, 2021 the State of Washington has adopted the following additional rules**

**[this informational page may be removed by jurisdictions utilizing the standard conditions]:**

5707.1.2 Coordination of permits. Permits across multiple authorities having jurisdiction shall be coordinated in accordance with Sections 5707.1.2.1 through 5707.1.2.4.

5707.1.2.1 Acceptance of permits issued by other authorities having jurisdiction. Local authorities having jurisdiction that allow mobile on demand fueling trucks may accept conforming permits issued and/or inspections performed by any other local authorities having jurisdiction in Washington state. Local authorities having jurisdiction that choose to accept conforming permits issued by other local authorities having jurisdiction in Washington state retain the right to enforce the provisions of this section.

5707.1.2.2 Local authorities having jurisdiction not offering operator or truck certification. A conforming operator or vehicle permit issued by one local authority having jurisdiction shall be recognized and accepted by all local authorities having jurisdiction in Washington state, if those local authority having jurisdictions allow mobile on demand fueling and do not offer such operator or truck certification. Under no circumstances will an issuing local authority having jurisdiction be expected to perform permissive inspections beyond their jurisdiction.

5707.1.2.3 Commencing permit issuance. When a local authority having jurisdiction that has previously authorized mobile fueling operations but not issued their own permits commences permit issuance for mobile fueling operations or vehicles, that local authority having jurisdiction shall continue to accept permits previously issued by another local authority having jurisdiction in Washington state for three months or until their expiration date, whichever is sooner.

5707.1.2.4 Permit record maintenance. Issuing local authorities having jurisdiction shall maintain a publicly available list of current permits or other information source to enable all parties to have information about whether permits are in good standing.

**2018 WA State Fire Code Conditions**

1. Mobile fueling vehicles shall comply with all applicable local, state, and federal requirements and shall be one of the following:
2. Type 1 Mobile Fueling Vehicle- A tank vehicle that complies with NFPA 385 and that has chassis-mounted tanks where the aggregate capacity does not exceed 1600 gallons.

1. Type 2 Mobile Fueling Vehicle- A vehicle with one or more chassis-mounted tanks or chassis-mounted containers, not to exceed 110 gallons capacity and having an aggregate capacity that does not exceed 800 gallons or the weight capacity of the vehicle in accordance with DOTn.
2. Type 3 Mobile Fueling Vehicle- A vehicle that carries a maximum aggregate capacity of 60 gallons of motor fuel in metal safety cans listed in accordance with UL 30 or other approved metal containers, each not to exceed 5 gallons in capacity.

[WA State Fire Code Section 5707.2.1]

1. Dispensing hose and nozzles shall be an approved type and listed. The dispensing hose shall not exceed 50 feet (15 240mm) in length. [WA State Fire Code Section 5707.5.1]
2. Mobile fueling vehicles with a chassis-mounted tank in excess of 110 gallons shall also comply with the requirements of Section 5706.6 and NFPA 385. [WA State Fire Code Section 5707.2.2(1)]
3. Safety cans and approved metal containers shall be secured to the mobile fueling vehicle except when in use. [WA State Fire Code Section 5707.2.2(3)]
4. Tanks or containers mounted in a trailer connected to a mobile fueling vehicle shall not be used for fueling into a motor vehicle. [WA State Fire Code Section 5707.2.2(4)]
5. A means of bonding the mobile fueling vehicle to the motor vehicle shall be provided and employed during fueling operations when metal-to-metal contact cannot be made between the nozzle and the fill opening. [WA State Fire Code Section 5707.5.1]
6. A listed Break-away device shall be provided at the nozzle on the mobile fueling vehicle unless the mobile fueling vehicle is equipped with an approved brake interlock tied to the nozzle holder. [WA State Fire Code Section 5707.5.2]
7. Mobile fueling vehicles shall be equipped with a listed shutoff valve assembly and a fuel limit switch set to a maximum of 30 gallons. [WA State Fire Code Section 5707.5.3]
8. Mobile fueling vehicles shall be provided with a fire extinguisher with a minimum rating of 4A:80BC and signage clearly indicating its location. [WA State Fire Code Section 5707.5.4]
9. Mobile fueling vehicles shall be provided with a minimum 5-gallon spill kit of an approved type. [WA State Fire Code Section 5707.5.5]
10. Signs prohibiting smoking or open flames within 25 feet of the vehicle or the point of fueling shall be prominently posted on the mobile fueling vehicle. [WA State Fire Code Section 5707.4.2]
11. Safety cones or other visual barriers shall be available on the mobile fueling vehicle to highlight the vehicle fueling area. No smoking signs shall be posted in vehicle fueling area. [WA State Fire Code Section 5707.6.3]
12. Drip pans or absorbent pillows shall be available on the mobile fueling vehicle. [WA State Fire Code Section 5707.6.2]